## Test Setup
Source | Bay | Switch | Position | IEC 61850 Address | Logic Diagram | [6 empty] | Assessment Signal | IEC 61850 Address
NUC | Q01 | QA1 | open | AA1D1Q01Q1QA1/CSWI1.Pos | ------------------------------------------------------------------------------------------------------------------------ |  |  |  |  | AND |  | Q01 QB1 Close Enable | AA1D1Q01Q1QB1/CILO1.EnaCls
NUC | Q01 | QB2 | open | AA1D1Q01Q1QB2/CSWI1.Pos | -------------------------------------------- |  |  | OR
ISIO | Q05 | QA1 | closed | AA1D1Q05Q1CBSW/XCBR1.Pos.stVal | ------------- | AND | [5 empty] | Command | IEC 61850 Address
ISIO | Q05 | QB1 | closed | AA1D1Q05Q1CBSW/XSWI1.Pos.stVal | ------------- |  | -------------- |  | -------- |  | ------------- | Q01 QB1 Close Command | AA1D1Q01Q1QB1/CSWI1.Pos
ISIO | Q05 | QB2 | closed | AA1D1Q05Q1CBSW/XSWI2.Pos.stVal | -------------
ISIO | Q05 | QC11 | open | AA1D1Q05Q1CBSW/XSWI3.Pos.stVal | -----------------------------------------------------------------------------------------------------------------------

## Test Steps
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Switchgear under test | Q01 QB1 | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE
Control Signal - Bay TR | Q01 QA1 | CLOSED | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN
Control Signal - Bay TR | Q01 QB2 | OPEN | OPEN | CLOSED | CLOSED | CLOSED | OPEN | OPEN | OPEN
Control Signal - Bay TR | Q01 QC9 | OPEN | OPEN | CLOSED | OPEN | OPEN | OPEN | OPEN | CLOSED
Control Signal - Bay BC | Q05 QA1 | OPEN | OPEN | OPEN | CLOSED | OPEN | OPEN | OPEN | OPEN
Control Signal - Bay BC | Q05 QB1 | OPEN | OPEN | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
Control Signal - Bay BC | Q05 QB2 | OPEN | OPEN | OPEN | CLOSED | CLOSED | OPEN | OPEN | OPEN
Control Signal - Bay BC | Q05 QC11 | OPEN | OPEN | OPEN | OPEN | OPEN | CLOSED | OPEN | OPEN
[5 empty] | CMD |  | CMD

## Signal Addresses
IED name | Signal Addresse
AA1D1Q01Q1 | AA1D1Q01Q1QA1/CSWI1.Pos
AA1D1Q01Q1 | AA1D1Q01Q1QB1/CSWI1.Pos
AA1D1Q01Q1 | AA1D1Q01Q1QB1/CILO1.EnaCls
AA1D1Q01Q1 | AA1D1Q01Q1QB2/CSWI1.Pos
AA1D1Q01Q1 | AA1D1Q01Q1QC9/CSWI1.Pos
AA1D1Q05Q1 | AA1D1Q05Q1CBSW/XCBR1.Pos.stVal
AA1D1Q05Q1 | AA1D1Q05Q1CBSW/XSWI1.Pos.stVal
AA1D1Q05Q1 | AA1D1Q05Q1CBSW/XSWI2.Pos.stVal
AA1D1Q05Q1 | AA1D1Q05Q1CBSW/XSWI3.Pos.stVal